## Slide 2: Disruptive Technologies
  This company specializes small, low power sensors
  In fact, the company boasts the world’s smallest wireless sensor
  It uses a jwt over https/ssl which should yield very strong security
  Several different types of connectors are available
  The connection is cloud-based

## Slide 3: Things that can be Monitored
  We have coded most of these into the connector and new ones can be added once their model is known:
    Temperature
    Humidity
    Proximity
    Touch/button
    Touch counter
    Water leak

## Slide 4: Disruptive Technologies API Set Up I
  Log into your Studio account
  Go to Service Accounts on the left side of the screen

## Slide 5: Disruptive Technologies API Set Up II
  Create a new Service Account email
  Create a new key. Doing this also gives you a secret which will not be available again, so save it somewhere. You will need both of these to gain API access.

## Slide 6: Disruptive Technologies Connector Tags in SkySpark
Creating a Disruptive Technologies connector:
  dis: Any Readable Name
  keyID_secret: Your key and secret go here separated by a . So that’s key.secret
  uri: `https://api.disruptive-technologies.com/v2/projects`
  serviceAccount: This looks like a complex email address and is just another key you need for API access
  The ngbTechPollFreq tag determines the minimum amount of time before the cache can be refreshed and how often the curVal values will be updated (which is from where both polling with intervals and COV come). The default value of 1min is good for detecting COV changes, but feel free to test lower numbers.
  Of course, these records will have the ngbTechConn and conn tags
These can be created in the connector app

## Slide 7: Disruptive Technologies Connector

## Slide 8: Disruptive Technologies Functions
ngbTechLearn – return a grid of all pre-coded points (only his points are available)
  read(ngbTechConn).ngbTechLearn
ngbTechSyncCur – force one or more cur points to sync
  readAll(ngbTechCur).ngbTechSyncCur
ngbTechSyncHis – force one or more his points to sync
  readAll(ngbTechHis).ngbTechSyncHis(lastMonth)
ngbTechPing – send ping to connector to check connection
  read(ngbTechConn).ngbTechPing
ngbTechCmd – send the connector a custom request
ngbTechToken – used to manually get a new token for requests (shouldn’t ever be needed)

## Slide 9: Getting Data for Disruptive Technologies Points Manually or with Automated Jobs
  Getting history data from Trend_Logs:
    Each point must have these tags:
      ngbTechConnRef (ref) which is a ref that points to the Connector
      ngbTechHis (str) which points to the Trend_Log object
      his (marker)
    Run the ngbTechSyncHis(timeRange) function
      generally as a task
      readAll(ngbTechHis).ngbTechSyncHis(null)
  Collecting current values (from curVal):
    Each point must have these tags:
      ngbTechConnRef (ref) which is a ref that points to the Connector
      ngbTechCur (str) which points to the point object
      his (marker)
      cur (marker)
      hisCollectCov (marker or number) for cov collection OR
      hisCollectInterval (duration) for polling
      Note: we recommend also using a hisCollectInterval of 24hr when using a hisCollectCov to catch faulty sensors.

## Slide 10: Basic Troubleshooting
Note that it is normal for a connection to close when it has no points in a watch for a given period of time
For larger systems, you may want to stagger your syncs
Notes on these Trend_Logs
Note that the Trend_Logs in our testing never went further back than a few days
Note that the Trend_Logs in our testing had data every 15 minutes, but they were not lined up with :00, :15, :30, and :45

## Slide 11: Getting Points via Code
() => do
varConn: read(ngbTechConn)
varConn.ngbTechLearn().map r => do
r = r.merge(
{
equipRef: read(equip)->id,
siteRef: read(site)->id,
hisCollectInterval: if (r->kind == "Number") 15min,
hisCollectCov: if (r->kind != "Number") marker(),
})
end.each r => commit(diff(null, r, {add}))
Run as a task in large systems to avoid a timeout error

## Slide 12: Getting History
Run as task in large systems to avoid a timeout error
(dates: null) => do
readAll(ngbTechHis).ngbTechSyncHis(dates)
end
Your initial import should be a set timeRange. Your reoccurring import will be set up in the Job App and will not need a parameter as it will take the default of null which always gets exactly the right amount of history.
For getting history from trend logs: